## Version Info
Description | Status | Function Code | Address-Decimal | Address - Hex
Internal machine version number: size 16 characters: small end mode | Read-only integer | 0X04 | 256 | 100
Inner machine version number: size 16 characters: big end mode | Read-only integer | 0X04 | 512 | 200
External machine version number: size 16 characters: big end mode | Read-only integer | 0X04 | 4000 | FA0
Driver version number: size 16 characters: big end mode | Read-only integer | 0X04 | 4256 | 10A0

## User operation commands
Description | Status | Function Code | Point Name | Address-Decimal | Address - Hex
0XFF00：Power on | Write switch only | 0X05 | Unit Power On | 0 | 0
0XFF00：Power off |  |  | Unit Power Off | 1 | 1
0XFF00：Reset |  |  | Reset command | 8 | 8
Forced defrost 0XFF00：Effective |  |  | 00# Module defrost command | 16 | 10
|  |  | 01# Module defrost command | 17 | 11
|  |  | 02# Module defrost command | 18 | 12
|  |  | 03# Module defrost command | 19 | 13
|  |  | 04# Module defrost command | 20 | 14
|  |  | 05#Module defrost command | 21 | 15
|  |  | 06#Module defrost command | 22 | 16
|  |  | 07#Module defrost command | 23 | 17
Initialization commands 0XFF00：Effective |  |  | Reserve | 128 | 80
|  |  | Factory parameter initialization | 129 | 81
|  |  | Inverter initialization | 130 | 82
|  |  | System maintenance initialization | 131 | 83
|  |  | Reserve | 132 | 84
|  |  | Reserve | 133 | 85
|  |  | Reserve | 134 | 86
|  |  | Reserve | 135 | 87
|  |  | Compressor runtime initialization | 136 | 88
|  |  | System runtime initialization | 137 | 89
Concentration Command 0XFF00：Effective |  |  | Zone A On | 1024 | 400
|  |  | Zone A Off | 1025 | 401
|  |  | Zone B On | 1026 | 402
|  |  | Zone B Off | 1027 | 403
|  |  | Hot water On | 1028 | 404
|  |  | Hot water Off | 1029 | 405
|  |  | Lower return pump timed on | 1030 | 406
|  |  | Lower return pump timed off | 1031 | 407
|  |  | Forced on hot water mode on | 1032 | 408
|  |  | Forced on hot water mode off | 1033 | 409
|  |  | Timed sterilization function on | 1034 | 40A
|  |  | Timed sterilization function off | 1035 | 40B
|  |  | Lower return pump sterilization on | 1036 | 40C
|  |  | Lower return pump sterilization off | 1037 | 40D
|  |  | Holiday leave mode on | 1038 | 40E
|  |  | Holiday away mode off | 1039 | 40F
|  |  | Holiday home mode on | 1040 | 410
|  |  | Holiday at home mode off | 1041 | 411
|  |  | Forced on tank electric heat on | 1042 | 412
|  |  | Forced on tank electric heat off | 1043 | 413
|  |  | Forced on auxiliary electric heat on | 1044 | 414
|  |  | Forced on auxiliary electric heat off | 1045 | 415
|  |  | Forced on external heat source on | 1046 | 416
|  |  | Forced on external heat source off | 1047 | 417
|  |  | Reserve | 1048 | 418
|  |  | Reserve | 1049 | 419
|  |  | Reserve | 1050 | 41A
|  |  | Floor heating preheat function on | 1051 | 41B
|  |  | Floor heating preheat function off | 1052 | 41C
|  |  | Floor heating drying function on | 1053 | 41D
|  |  | Floor heating drying function off | 1054 | 41E
|  |  | Air evacuation test run on | 1055 | 41F
|  |  | Air evacuation test run off | 1056 | 420
|  |  | Water pump test run on | 1057 | 421
|  |  | Water pump test run off | 1058 | 422
|  |  | Cooling test run on | 1059 | 423
|  |  | Cooling test run off | 1060 | 424
|  |  | Heating test run on | 1061 | 425
|  |  | Heating test run off | 1062 | 426
|  |  | Reserve | 1063 | 427
|  |  | Reserve | 1064 | 428
|  |  | Hot water test run on | 1065 | 429
|  |  | Hot water test run off | 1066 | 42A
|  |  | Reserve | 1067 | 42B
|  |  | Reserve | 1068 | 42C
|  |  | Ability test on | 1069 | 42D
|  |  | Ability test off | 1070 | 42E
|  |  | Fluorine collection on | 1071 | 42F
|  |  | Fluorine collection off | 1072 | 430
|  |  | Mute mode on | 1073 | 431
|  |  | Mute mode off | 1074 | 432
|  |  | Mute level 1 | 1075 | 433
|  |  | Quiet level 2 | 1076 | 434
|  |  | Holiday away from home heating mode use | 1077 | 435
|  |  | Holiday away from home heating mode disabled | 1078 | 436
|  |  | Holiday away from home hot water mode use | 1079 | 437
|  |  | Holiday away from home hot water mode disable | 1080 | 438
|  |  | Manual debugging on | 1081 | 439
|  |  | Manual debugging off | 1082 | 43A
|  |  | Reserve | 1083 | 43B
|  |  | Reserve | 1084 | 43C
|  |  | Cancel Preheat | 1085 | 43D
|  |  | Quick Preheat | 1086 | 43E
Manual debugging 0XFF00：Position 0X0000：Reset |  |  | Defrost | 2048 | 800
|  |  | Fault | 2049 | 801
|  |  | External heat source | 2050 | 802
|  |  | Solenoid 3-way valve 1 | 2051 | 803
|  |  | Solenoid 3-way valve 3 | 2052 | 804
|  |  | Solenoid 3-way valve 2 | 2053 | 805
|  |  | Anti-freeze heating tape | 2054 | 806
|  |  | Lower return water pump | 2055 | 807
|  |  | Solar water pump | 2056 | 808
|  |  | Mixing water pump | 2057 | 809
|  |  | Water tank electric heating | 2058 | 80A
|  |  | Auxiliary electric heating 1 | 2059 | 80B
|  |  | Auxiliary electric heating 2 | 2060 | 80C
|  |  | External circulation pump | 2061 | 80D
|  |  | Inverter water pump | 2062 | 80E
|  |  | Crankshaft electric heating 1 | 2063 | 80F
|  |  | Crankshaft electric heating 2 | 2064 | 810
|  |  | Chassis heating | 2065 | 811
|  |  | Four-way valve | 2066 | 812
|  |  | Liquid injection valve | 2067 | 813

## Read and Write
Point Name | Status | Function Code | Address-Decimal | Address - Hex | Description
Year: 2000~2099 | Write only integers | 0X10 | 5000 | 1388 | 0. Do not read, and write in one frame 1. send down once after successful power-up communication, then may send down once per minute thereafter
Month: 1~12 |  |  | 5001 | 1389
Day:1~31 |  |  | 5002 | 138A
Week:0~6:Sunday~Saturday |  |  | 5003 | 138B
Hour:0~23 |  |  | 5004 | 138C
Minute:0~59 |  |  | 5005 | 138D
Seconds:0~59 |  |  | 5006 | 138E

## Unit Info
Point Name | Address - Decimal | Address - Hex | Description | Status | Function code
Unit Status | 768 | 300 | B0: Unit in standby mode B1: Unit in start-up B2: Unit running B3: Unit is shutting down B4: Unit in serious alarm B5. B6. B7. B8: Unit preheating B9: Unit is faulty B10: Unit defrosted B11: Unit defrosted B12. B13. B14. B15: | Read-only integer | 0X04
Number of presses in module 0# | 769 | 301
Air conditioning mode | 770 | 302 | Please refer to the "Mode settings" in the parameter table
Current operating mode | 771 | 303 | 0: none; 1: cooling; 2: heating; 3: automatic; 4: hot water
Can adjust target Temp. | 772 | 304 | Unit 0.1°C
Able to adjust control Temp. | 773 | 305 | Unit 0.1°C
Modules used | 791 | 317 | B0: 0# module use disabled B1: 1# module use disabled B2: 2# module use disabled B3: 3# module use disabled B4: 4# module use disabled B5: 5# module use disabled B6: 6# module use disabled B7: 7# module use disabled B8. B9. B10. B11. B12. B13. B14. B15:
Number of modules | 792 | 318
Operating status | 793 | 319 | 0: Unit in standby mode 1: Unit is starting up 2: Unit running 3: Unit is shutting down 4: Unit in serious alarm
Upper Limit of A-Zone Set Temp. | 794 | 31A | Cooling operation mode. Cooling trial run: 7°C Fluorine collection: 5°C Capacity test: 5°C Water Temp. control: upper limit of cooling set Temp. Room Temp. control: [Cooling set room Temp.] maximum Heating operation mode. Heating test run: 35°C Capacity test: 62°C Underfloor heating drying: Underfloor heating drying can adjust the target Temp. Underfloor heating preheating: [Underfloor heating preheating Temp. Water Temp. control: heating set Temp. upper limit Room Temp. control: [Heating set room Temp.] maximum
Lower Limit of A-Zone Set Temp. | 795 | 31B | Cooling operating mode. Refrigeration trial run: 7°C Fluorine collection: 5°C Capacity test: 5°C Water Temp. control: cooling set Temp. lower limit Room Temp. control: [Cooling set room Temp.] min Heating operation mode. Heating test run: 35°C Capacity test: 62°C Underfloor heating drying: Underfloor heating drying capable of adjusting target Temp. Underfloor heating preheating: [Underfloor heating preheating Temp. Water Temp. control: heating set Temp. lower limit Room Temp. control: [Heating set room Temp.] min.
Upper Limit of B-Zone Set Temp. | 796 | 31C | Cooling operating mode. Refrigeration trial run: 7°C Fluorine collection: 5°C Capacity test: 5°C For water Temp. control: upper limit of cooling set Temp. in zone B Room Temp. control: [Cooling set room Temp.] maximum Heating operation mode. Heating test run: 35°C Capacity test: 62°C Underfloor heating drying: Underfloor heating drying capable of adjusting target Temp. Underfloor heating preheating: [Underfloor heating preheating Temp. Water Temp. control: heating set Temp. upper limit Room Temp. control: [Heating set room Temp. (B)] maximum
Lower Limit of B-Zone Set Temp. | 797 | 31D | Cooling operation mode: Refrigeration trial run: 7°C Fluorine collection: 5°C Capacity test: 5°C Water Temp. control: lower limit of refrigeration set Temp. Room Temp. control : [Cooling set room Temp.] min. Heating operation mode. Heating test run: 35°C Capacity test: 62°C Underfloor heating drying: Underfloor heating drying capable of adjusting target Temp. Underfloor heating preheating: [Underfloor heating preheating Temp. Water Temp. control: heating set Temp. lower limit Room Temp. control: [Heating set room Temp. (B)] min.
Upper Limit of Hot Water Set Temp. | 798 | 31E | Hot water making test run: 55°C Timed sterilisation operation: [Hot water set Temp. Holiday away mode operation: [Holiday away from home hot water Free electricity forced operation: 70°C Other: [heating return Temp. upper limit]
Lower Limit of Hot Water Set Temp. | 799 | 31F | Hot water making trial run: 55°C Timed sterilisation operation: [Hot water set Temp. Holiday away mode operation: [Holiday away from home hot water Free electricity forced operation: 70℃ Other: [heating return Temp. lower limit]
Upper Limit of Cooling Set Temp. | 800 | 320 | Return water: [Cooling return Temp. upper limit]; Discharge water: [Cooling return Temp. upper limit] - 5. Note: If the range of [Cooling Set Temp.] is exceeded, the range of [Cooling Set Temp.] prevails. The purpose is to prevent EEPROM errors from being reported.
Lower Limit of Cooling Set Temp. | 801 | 321 | Return water: [Cooling return Temp. lower limit]; Discharge water: [Cooling return Temp. lower limit] - 5 Note: If the range of [Cooling set Temp.] is exceeded, the range of [Cooling set Temp.] prevails. The purpose is to prevent the reporting of EEPROM errors.
Upper Limit of Heating Set Temp. | 802 | 322 | Return water: [Heating return Temp. upper limit]; Discharge water: [Heating return Temp. upper limit] + 5 Note: If the range of [Heating set Temp.] is exceeded, the range of [Heating set Temp.] prevails. The purpose is to prevent the reporting of EEPROM errors.
Lower Limit of Heating Set Temp. | 803 | 323 | Return water: [Heating return Temp. lower limit]; Discharge water: [Heating return Temp. lower limit] + 5 Note: If the range of [Heating set Temp.] is exceeded, the range of [Heating set Temp.] prevails. The purpose is to prevent the reporting of EEPROM errors.
Upper Limit of B-Zone Cooling Set Temp. | 804 | 324 | Return water: [Cooling return Temp. upper limit]; Discharge water: [Cooling return Temp. upper limit] - 5 Note: If the range of [Cooling set Temp.] is exceeded, the range of [Cooling set Temp.] prevails. The purpose is to prevent the reporting of EEPROM errors.
Lower Limit of B-Zone Cooling Set Temp. | 805 | 325 | Return water: [Cooling return Temp. lower limit]; Discharge water: [Cooling return Temp. lower limit] - 5 Note: If the range of [Cooling set Temp.] is exceeded, the range of [Cooling set Temp.] prevails. The purpose is to prevent the reporting of EEPROM errors.
Upper Limit of B-Zone Heating Set Temp. | 806 | 326 | Return water: [Heating return Temp. upper limit]; Discharge water: [Heating return Temp. upper limit] + 5 Note: If the range of [Heating set Temp.] is exceeded, the range of [Heating set Temp.] prevails. The purpose is to prevent the reporting of EEPROM errors.
Lower Limit of B-Zone Heating Set Temp. | 807 | 327 | Return water: [Heating return Temp. lower limit]; Discharge water: [Heating return Temp. lower limit] + 5 Note: If the range of [Heating set Temp.] is exceeded, the range of [Heating set Temp.] prevails. The purpose is to prevent the reporting of EEPROM errors.
Left Minutes for Preheating | 808 | 328
Parameter initialisation status | 809 | 329 | 0: No action 1: Action execution started 2: Action execution in progress 3: Action execution successful 4: Action execution failed
Test run | 910 | 38E | B0: Air evacuation test run B1: Pump test run B2: Refrigeration test run B3: Heating test run B4: Hot water test run
Run flag 0 | 912 | 390 | B0: Zone A operating sign B1: Zone B operating sign B2: Hot water operating sign B3: Timed down return pump operating sign B4: Strong on hot water mode function operating sign B5: Timed sterilisation operating sign B6: Downstream pump sterilisation operating sign B7: Holiday away mode operating sign B8: Holiday at home mode operating sign B9: Forced on tank electric heating operating sign B10: Forced on auxiliary electric heating operating sign B11: Forced on external heat source operating sign B12: Underfloor heating preheating operating sign B13: Underfloor heating drying function operating sign B14: Capacity test operating sign B15: Fluorine collection operating sign
Run flag 1 | 913 | 391 | B0: Silent mode sign B1: Silent mode level: 0: level 1; 1: level 2
0# Number of Module Compressors | 1000 | 3E8
1# Number of Module Compressors | 1001 | 3E9
2# Number of Module Compressors | 1002 | 3EA
3# Number of Module Compressors | 1003 | 3EB
4# Number of Module Compressors | 1004 | 3EC
5# Number of Module Compressors | 1005 | 3ED
6# Number of Module Compressors | 1006 | 3EE
7# Number of Module Compressors | 1007 | 3EF
System Runtime | 1024 | 400 | Umit:h
Compressor Run Time | 1025 | 401
Compressor Run Time | 1026 | 402
Compressor Run Time | 1027 | 403
Compressor Run Time | 1028 | 404
Compressor Run Time | 1029 | 405
Compressor Run Time | 1030 | 406
Compressor Run Time | 1031 | 407
Compressor Run Time | 1032 | 408
Inverter Unit Status | 1033 | 409 | Bit 0: Power-up ready Bit 8: Standby Bit 1: Ready for operation Bit 9: Standby Bit 2: In operation Bit 10: Standby Bit 3: Fault Bit 11: Standby Bit 4: OFF2 Stop active (0 active) Bit 12: Standby Bit 5: OFF3 In standby (0 valid) Bit 13: Standby Bit 6: Charging contactor disconnected Bit 14: In positive operation Bit 7: Alarm (in non-stop alarm) Bit 15: Standby
Operating Speed | 1034 | 40A | Unit 0.1rps
Module Temp. | 1035 | 40B | Unit 0.1°C
Output Power | 1036 | 40C | Unit 0.01KW
Given Speed | 1037 | 40D | Unit 0.1rps
Output Current | 1038 | 40E | Unit 0.1A
Output Torque | 1039 | 40F | Unit 0.1%
Output Voltage | 1040 | 410 | Unit 0.1V
Bus Voltage | 1041 | 411 | Unit 0.1V
Error Code | 1042 | 412 | A value of 0 means no fault, otherwise it means the current fault code, see the manufacturer's instruction manual "Inverter type fault" for details
Inverter Input Current | 1043 | 413 | Unit 0.1A
PFC Temp. | 1044 | 414 | Unit 0.1°C
Current Speed | 1045 | 415 | Unit 0.1rps
Frequency Limit Information | 1046 | 416 | See "Frequency limit information for inverters" in the manufacturer's manual
| 1047 | 417
| 1048 | 418

## Analog
Read-only integer; Function code: 04 | [21 empty] | Description. -32700(0x8044) indicates probe not present, -32701(0x8043) indicates probe fault, -32702(0x8042) indicates that the probe is disconnected , -32703(0x8041) indicates that the probe is short-circuited
Module Information |  | Address ( Decimal ) | [7 empty] | Address ( Hex ) | [7 empty] | System Information |  | Address ( Decimal ) | Address ( Hex )
Point Name | Unit | 0#Module | 1#Module | 2#Module | 3#Module | 4#Module | 5#Module | 6#Module | 7#Module | 0#Module | 1#Module | 2#Module | 3#Module | 4#Module | 5#Module | 6#Module | 7#Module | Point Name | Unit
\ |  | 1300 | 1556 | 1812 | 2068 | 2324 | 2580 | 2836 | 3092 | 514 | 614 | 714 | 814 | 914 | A14 | B14 | C14 | Room temperature | 0.1℃ | 3348 | D14
Main circuit EEV opening | 步 | 1301 | 1557 | 1813 | 2069 | 2325 | 2581 | 2837 | 3093 | 515 | 615 | 715 | 815 | 915 | A15 | B15 | C15 | \ |  | 3349 | D15
Auxiliary EEV opening | 步 | 1302 | 1558 | 1814 | 2070 | 2326 | 2582 | 2838 | 3094 | 516 | 616 | 716 | 816 | 916 | A16 | B16 | C16 | Ambient temperature | 0.1℃ | 3350 | D16
Fin temperature | 0.1℃ | 1303 | 1559 | 1815 | 2071 | 2327 | 2583 | 2839 | 3095 | 517 | 617 | 717 | 817 | 917 | A17 | B17 | C17 | Hot water tank temperature | 0.1℃ | 3351 | D17
Exhaust temperature | 0.1℃ | 1304 | 1560 | 1816 | 2072 | 2328 | 2584 | 2840 | 3096 | 518 | 618 | 718 | 818 | 918 | A18 | B18 | C18 | \ | 0.1℃ | 3352 | D18
Suction temperature | 0.1℃ | 1305 | 1561 | 1817 | 2073 | 2329 | 2585 | 2841 | 3097 | 519 | 619 | 719 | 819 | 919 | A19 | B19 | C19 | Total system water outlet temperature | 0.1℃ | 3353 | D19
\ |  | 1306 | 1562 | 1818 | 2074 | 2330 | 2586 | 2842 | 3098 | 51A | 61A | 71A | 81A | 91A | A1A | B1A | C1A | Solar temperature | 0.1℃ | 3354 | D1A
\ |  | 1307 | 1563 | 1819 | 2075 | 2331 | 2587 | 2843 | 3099 | 51B | 61B | 71B | 81B | 91B | A1B | B1B | C1B | Buffer tank upper temperature | 0.1℃ | 3355 | D1B
Evaporation saturation temperature | 0.1℃ | 1308 | 1564 | 1820 | 2076 | 2332 | 2588 | 2844 | 3100 | 51C | 61C | 71C | 81C | 91C | A1C | B1C | C1C | Buffer tank lower temperature | 0.1℃ | 3356 | D1C
Condensation saturation temperature | 0.1℃ | 1309 | 1565 | 1821 | 2077 | 2333 | 2589 | 2845 | 3101 | 51D | 61D | 71D | 81D | 91D | A1D | B1D | C1D | Total air conditioning water discharge temperature | 0.1℃ | 3357 | D1D
Low pressure | 0.1bar | 1310 | 1566 | 1822 | 2078 | 2334 | 2590 | 2846 | 3102 | 51E | 61E | 71E | 81E | 91E | A1E | B1E | C1E | \ |  | 3358 | D1E
High pressure | 0.1bar | 1311 | 1567 | 1823 | 2079 | 2335 | 2591 | 2847 | 3103 | 51F | 61F | 71F | 81F | 91F | A1F | B1F | C1F | \\ |  | 3359 | D1F
Main valve target superheat | 0.1℃ | 1312 | 1568 | 1824 | 2080 | 2336 | 2592 | 2848 | 3104 | 520 | 620 | 720 | 820 | 920 | A20 | B20 | C20 | \\ |  | 3360 | D20
Main valve current superheat | 0.1℃ | 1313 | 1569 | 1825 | 2081 | 2337 | 2593 | 2849 | 3105 | 521 | 621 | 721 | 821 | 921 | A21 | B21 | C21 | \ |  | 3361 | D21
Auxiliary valve target overheat | 0.1℃ | 1314 | 1570 | 1826 | 2082 | 2338 | 2594 | 2850 | 3106 | 522 | 622 | 722 | 822 | 922 | A22 | B22 | C22 | Underfloor heating inlet water temperature | 0.1℃ | 3362 | D22
Auxiliary valve currently overheating | 0.1℃ | 1315 | 1571 | 1827 | 2083 | 2339 | 2595 | 2851 | 3107 | 523 | 623 | 723 | 823 | 923 | A23 | B23 | C23 | Solenoid 3-way valve 1 status |  | 3363 | D23
\ |  | 1316 | 1572 | 1828 | 2084 | 2340 | 2596 | 2852 | 3108 | 524 | 624 | 724 | 824 | 924 | A24 | B24 | C24 | Solenoid 3-way valve 2 status |  | 3364 | D24
\ |  | 1317 | 1573 | 1829 | 2085 | 2341 | 2597 | 2853 | 3109 | 525 | 625 | 725 | 825 | 925 | A25 | B25 | C25 | Solenoid 3-way valve 3 status |  | 3365 | D25
Frost-free operation ring fin difference | 0.1℃ | 1318 | 1574 | 1830 | 2086 | 2342 | 2598 | 2854 | 3110 | 526 | 626 | 726 | 826 | 926 | A26 | B26 | C26 | \ |  | 3366 | D26
Variable frequency target speed | 0.1rps | 1319 | 1575 | 1831 | 2087 | 2343 | 2599 | 2855 | 3111 | 527 | 627 | 727 | 827 | 927 | A27 | B27 | C27 | \ |  | 3367 | D27
Variable frequency current speed | 0.1rps | 1320 | 1576 | 1832 | 2088 | 2344 | 2600 | 2856 | 3112 | 528 | 628 | 728 | 828 | 928 | A28 | B28 | C28 | \ |  | 3368 | D28
Variable frequency output voltage | 0.1V | 1321 | 1577 | 1833 | 2089 | 2345 | 2601 | 2857 | 3113 | 529 | 629 | 729 | 829 | 929 | A29 | B29 | C29 | \ |  | 3369 | D29
Inverter output current | 0.1A | 1322 | 1578 | 1834 | 2090 | 2346 | 2602 | 2858 | 3114 | 52A | 62A | 72A | 82A | 92A | A2A | B2A | C2A
Inverter module temperature | 0.1℃ | 1323 | 1579 | 1835 | 2091 | 2347 | 2603 | 2859 | 3115 | 52B | 62B | 72B | 82B | 92B | A2B | B2B | C2B
Frequency limit information |  | 1324 | 1580 | 1836 | 2092 | 2348 | 2604 | 2860 | 3116 | 52C | 62C | 72C | 82C | 92C | A2C | B2C | C2C
Inverter input current | 0.1A | 1325 | 1581 | 1837 | 2093 | 2349 | 2605 | 2861 | 3117 | 52D | 62D | 72D | 82D | 92D | A2D | B2D | C2D
Variable frequency output power | 0.01 | 1326 | 1582 | 1838 | 2094 | 2350 | 2606 | 2862 | 3118 | 52E | 62E | 72E | 82E | 92E | A2E | B2E | C2E
Fan 1 target operation | rpm | 1327 | 1583 | 1839 | 2095 | 2351 | 2607 | 2863 | 3119 | 52F | 62F | 72F | 82F | 92F | A2F | B2F | C2F
Fan 1 current speed | rpm | 1328 | 1584 | 1840 | 2096 | 2352 | 2608 | 2864 | 3120 | 530 | 630 | 730 | 830 | 930 | A30 | B30 | C30
Fan 2 target operation | rpm | 1329 | 1585 | 1841 | 2097 | 2353 | 2609 | 2865 | 3121 | 531 | 631 | 731 | 831 | 931 | A31 | B31 | C31
Fan 2 current speed | rpm | 1330 | 1586 | 1842 | 2098 | 2354 | 2610 | 2866 | 3122 | 532 | 632 | 732 | 832 | 932 | A32 | B32 | C32
\ |  | 1331 | 1587 | 1843 | 2099 | 2355 | 2611 | 2867 | 3123 | 533 | 633 | 733 | 833 | 933 | A33 | B33 | C33
\ |  | 1332 | 1588 | 1844 | 2100 | 2356 | 2612 | 2868 | 3124 | 534 | 634 | 734 | 834 | 934 | A34 | B34 | C34
Refrigerant gas side temperature | 0.1℃ | 1333 | 1589 | 1845 | 2101 | 2357 | 2613 | 2869 | 3125 | 535 | 635 | 735 | 835 | 935 | A35 | B35 | C35
Refrigerant liquid side temperature | 0.1℃ | 1334 | 1590 | 1846 | 2102 | 2358 | 2614 | 2870 | 3126 | 536 | 636 | 736 | 836 | 936 | A36 | B36 | C36
\ |  | 1335 | 1591 | 1847 | 2103 | 2359 | 2615 | 2871 | 3127 | 537 | 637 | 737 | 837 | 937 | A37 | B37 | C37
\ |  | 1336 | 1592 | 1848 | 2104 | 2360 | 2616 | 2872 | 3128 | 538 | 638 | 738 | 838 | 938 | A38 | B38 | C38
\ |  | 1337 | 1593 | 1849 | 2105 | 2361 | 2617 | 2873 | 3129 | 539 | 639 | 739 | 839 | 939 | A39 | B39 | C39
\ |  | 1338 | 1594 | 1850 | 2106 | 2362 | 2618 | 2874 | 3130 | 53A | 63A | 73A | 83A | 93A | A3A | B3A | C3A
\ |  | 1339 | 1595 | 1851 | 2107 | 2363 | 2619 | 2875 | 3131 | 53B | 63B | 73B | 83B | 93B | A3B | B3B | C3B
\ |  | 1340 | 1596 | 1852 | 2108 | 2364 | 2620 | 2876 | 3132 | 53C | 63C | 73C | 83C | 93C | A3C | B3C | C3C
\ |  | 1341 | 1597 | 1853 | 2109 | 2365 | 2621 | 2877 | 3133 | 53D | 63D | 73D | 83D | 93D | A3D | B3D | C3D
\ |  | 1342 | 1598 | 1854 | 2110 | 2366 | 2622 | 2878 | 3134 | 53E | 63E | 73E | 83E | 93E | A3E | B3E | C3E
\ |  | 1343 | 1599 | 1855 | 2111 | 2367 | 2623 | 2879 | 3135 | 53F | 63F | 73F | 83F | 93F | A3F | B3F | C3F
\ |  | 1344 | 1600 | 1856 | 2112 | 2368 | 2624 | 2880 | 3136 | 540 | 640 | 740 | 840 | 940 | A40 | B40 | C40
\ |  | 1345 | 1601 | 1857 | 2113 | 2369 | 2625 | 2881 | 3137 | 541 | 641 | 741 | 841 | 941 | A41 | B41 | C41
\ |  | 1346 | 1602 | 1858 | 2114 | 2370 | 2626 | 2882 | 3138 | 542 | 642 | 742 | 842 | 942 | A42 | B42 | C42
\ |  | 1347 | 1603 | 1859 | 2115 | 2371 | 2627 | 2883 | 3139 | 543 | 643 | 743 | 843 | 943 | A43 | B43 | C43
Plate exchange return water temperature | 0.1℃ | 1348 | 1604 | 1860 | 2116 | 2372 | 2628 | 2884 | 3140 | 544 | 644 | 744 | 844 | 944 | A44 | B44 | C44
Plate exchange outlet water temperature | 0.1℃ | 1349 | 1605 | 1861 | 2117 | 2373 | 2629 | 2885 | 3141 | 545 | 645 | 745 | 845 | 945 | A45 | B45 | C45
Total outlet temperature | 0.1℃ | 1350 | 1606 | 1862 | 2118 | 2374 | 2630 | 2886 | 3142 | 546 | 646 | 746 | 846 | 946 | A46 | B46 | C46
Ambient temperature | 0.1℃ | 1351 | 1607 | 1863 | 2119 | 2375 | 2631 | 2887 | 3143 | 547 | 647 | 747 | 847 | 947 | A47 | B47 | C47
Inverter pump target speed | rpm | 1352 | 1608 | 1864 | 2120 | 2376 | 2632 | 2888 | 3144 | 548 | 648 | 748 | 848 | 948 | A48 | B48 | C48
Inverter pump current flow rate | L/h | 1353 | 1609 | 1865 | 2121 | 2377 | 2633 | 2889 | 3145 | 549 | 649 | 749 | 849 | 949 | A49 | B49 | C49
Inverter pump control signal | % | 1354 | 1610 | 1866 | 2122 | 2378 | 2634 | 2890 | 3146 | 54A | 64A | 74A | 84A | 94A | A4A | B4A | C4A
Inverter pump feedback signal | % | 1355 | 1611 | 1867 | 2123 | 2379 | 2635 | 2891 | 3147 | 54B | 64B | 74B | 84B | 94B | A4B | B4B | C4B
Inverter pump fault information |  | 1356 | 1612 | 1868 | 2124 | 2380 | 2636 | 2892 | 3148 | 54C | 64C | 74C | 84C | 94C | A4C | B4C | C4C
Unit calibration capacity |  | 1357 | 1613 | 1869 | 2125 | 2381 | 2637 | 2893 | 3149 | 54D | 64D | 74D | 84D | 94D | A4D | B4D | C4D
Unit current capacity |  | 1358 | 1614 | 1870 | 2126 | 2382 | 2638 | 2894 | 3150 | 54E | 64E | 74E | 84E | 94E | A4E | B4E | C4E

## 04-Input and Output
Read-only integer; Function code: 04
Point Name | Description | Address ( Decimal ) | [7 empty] | Address ( Hex ) | [7 empty] | Point Name | Description | Address ( Decimal ) | Address ( Hex )
|  | 0#Module | 1#Module | 2#Module | 3#Module | 4#Module | 5#Module | 6#Module | 7#Module | 0#Module | 1#Module | 2#Module | 3#Module | 4#Module | 5#Module | 6#Module | 7#Module
Compressor Relay Outputs | B0: Inverter press B1: Four-way valve B2: Liquid injection valve B3. B4. B5: Crankshaft electric heating 1 B6. B7: Crankshaft electric heating 2 | 1283 | 1539 | 1795 | 2051 | 2307 | 2563 | 2819 | 3075 | 503 | 603 | 703 | 803 | 903 | A03 | B03 | C03 | System Relay Outputs | B0: Defrost indication B1: Fault indication B2: External heat source B3: Solenoid 3-way valve 1 B4: Solenoid 3-way valve 3 B5: Solenoid 3-way valve 2 B6: Tank electric heating B7. B8: Lower return pump B9: Solar water pump B10: Mixing water pump B11: External circulation pump B12. B13: | 3331 | D03
Unit relay outputs | B0: Inverter water pump B1: Auxiliary electric heating 1 B2: Auxiliary electric heating 2 B3: Sump electric heating B4: Anti-freeze electric heating belt B5. B6. B7: | 1285 | 1541 | 1797 | 2053 | 2309 | 2565 | 2821 | 3077 | 505 | 605 | 705 | 805 | 905 | A05 | B05 | C05
Compressor switching input | B0: Press low pressure B1: Press high pressure B2. B3. B4. B5. B6. B7: | 1286 | 1542 | 1798 | 2054 | 2310 | 2566 | 2822 | 3078 | 506 | 606 | 706 | 806 | 906 | A06 | B06 | C06 | System Switch Inputs | B0. B1: In-line switch B2. B3. B4. B5. B6. B7. B8: Tank electrical feedback B9: Thermostat C signal B10: Thermostat H signal B11: Solar signal B12: Smart grid SG signal B13: Smart grid EVU signal | 3334 | D06
Unit switch input | B0: Auxiliary electric feedback B1: Water flow switch B2. B3. B4. B5. B6. B7: | 1288 | 1544 | 1800 | 2056 | 2312 | 2568 | 2824 | 3080 | 508 | 608 | 708 | 808 | 908 | A08 | B08 | C08
Press status | B13: Defrosting in progress | 1289 | 1545 | 1801 | 2057 | 2313 | 2569 | 2825 | 3081 | 509 | 609 | 709 | 809 | 909 | A09 | B09 | C09

## 02-Input and Output
Read-only switch；Function code: 04
Point Name | Description | Address ( Decimal ) | [7 empty] | Address ( Hex ) | [7 empty] | Point Name | Description | Address ( Decimal ) | Address ( Hex )
|  | 0#Module | 1#Module | 2#Module | 3#Module | 4#Module | 5#Module | 6#Module | 7#Module | 0#Module | 1#Module | 2#Module | 3#Module | 4#Module | 5#Module | 6#Module | 7#Module
Inverter compressors | Compressor relay output 1 | 768 | 1536 | 2304 | 3072 | 3840 | 4608 | 5376 | 6144 | 300 | 600 | 900 | C00 | F00 | 1200 | 1500 | 1800 | System relay output | Defrost indication | 0 | 0
Four-way valves |  | 769 | 1537 | 2305 | 3073 | 3841 | 4609 | 5377 | 6145 | 301 | 601 | 901 | C01 | F01 | 1201 | 1501 | 1801 |  | Fault indication | 1 | 1
Liquid injection valves |  | 770 | 1538 | 2306 | 3074 | 3842 | 4610 | 5378 | 6146 | 302 | 602 | 902 | C02 | F02 | 1202 | 1502 | 1802 |  | External heat source | 2 | 2
Reserve |  | 771 | 1539 | 2307 | 3075 | 3843 | 4611 | 5379 | 6147 | 303 | 603 | 903 | C03 | F03 | 1203 | 1503 | 1803 |  | Solenoid 3-way valve 1 | 3 | 3
Reserve |  | 772 | 1540 | 2308 | 3076 | 3844 | 4612 | 5380 | 6148 | 304 | 604 | 904 | C04 | F04 | 1204 | 1504 | 1804 |  | Solenoid 3-way valve 3 | 4 | 4
Crankshaft electric heating 1 |  | 773 | 1541 | 2309 | 3077 | 3845 | 4613 | 5381 | 6149 | 305 | 605 | 905 | C05 | F05 | 1205 | 1505 | 1805 |  | Solenoid 3-way valve 2 | 5 | 5
Reserve |  | 774 | 1542 | 2310 | 3078 | 3846 | 4614 | 5382 | 6150 | 306 | 606 | 906 | C06 | F06 | 1206 | 1506 | 1806 |  | Water tank electric heating | 6 | 6
Crankshaft electric heating 2 |  | 775 | 1543 | 2311 | 3079 | 3847 | 4615 | 5383 | 6151 | 307 | 607 | 907 | C07 | F07 | 1207 | 1507 | 1807 |  | Reserve | 7 | 7
Reserve |  | 776 | 1544 | 2312 | 3080 | 3848 | 4616 | 5384 | 6152 | 308 | 608 | 908 | C08 | F08 | 1208 | 1508 | 1808 |  | Lower return water pump | 8 | 8
Reserve |  | 777 | 1545 | 2313 | 3081 | 3849 | 4617 | 5385 | 6153 | 309 | 609 | 909 | C09 | F09 | 1209 | 1509 | 1809 |  | Solar water pump | 9 | 9
Reserve |  | 778 | 1546 | 2314 | 3082 | 3850 | 4618 | 5386 | 6154 | 30A | 60A | 90A | C0A | F0A | 120A | 150A | 180A |  | Mixing water pump | 10 | A
Reserve |  | 779 | 1547 | 2315 | 3083 | 3851 | 4619 | 5387 | 6155 | 30B | 60B | 90B | C0B | F0B | 120B | 150B | 180B |  | External circulation pump | 11 | B
Reserve |  | 780 | 1548 | 2316 | 3084 | 3852 | 4620 | 5388 | 6156 | 30C | 60C | 90C | C0C | F0C | 120C | 150C | 180C |  | Reserve | 12 | C
Reserve |  | 781 | 1549 | 2317 | 3085 | 3853 | 4621 | 5389 | 6157 | 30D | 60D | 90D | C0D | F0D | 120D | 150D | 180D |  | Reserve | 13 | D
Reserve |  | 782 | 1550 | 2318 | 3086 | 3854 | 4622 | 5390 | 6158 | 30E | 60E | 90E | C0E | F0E | 120E | 150E | 180E |  | Reserve | 14 | E
Reserve |  | 783 | 1551 | 2319 | 3087 | 3855 | 4623 | 5391 | 6159 | 30F | 60F | 90F | C0F | F0F | 120F | 150F | 180F |  | Reserve | 15 | F
Inverter water pump | Unit relay output | 800 | 1568 | 2336 | 3104 | 3872 | 4640 | 5408 | 6176 | 320 | 620 | 920 | C20 | F20 | 1220 | 1520 | 1820
Auxiliary electric heating 1 |  | 801 | 1569 | 2337 | 3105 | 3873 | 4641 | 5409 | 6177 | 321 | 621 | 921 | C21 | F21 | 1221 | 1521 | 1821
Auxiliary electric heating 2 |  | 802 | 1570 | 2338 | 3106 | 3874 | 4642 | 5410 | 6178 | 322 | 622 | 922 | C22 | F22 | 1222 | 1522 | 1822
Chassis electric heating |  | 803 | 1571 | 2339 | 3107 | 3875 | 4643 | 5411 | 6179 | 323 | 623 | 923 | C23 | F23 | 1223 | 1523 | 1823
Anti-freeze electric heating belt |  | 804 | 1572 | 2340 | 3108 | 3876 | 4644 | 5412 | 6180 | 324 | 624 | 924 | C24 | F24 | 1224 | 1524 | 1824
Reserve |  | 805 | 1573 | 2341 | 3109 | 3877 | 4645 | 5413 | 6181 | 325 | 625 | 925 | C25 | F25 | 1225 | 1525 | 1825
Reserve |  | 806 | 1574 | 2342 | 3110 | 3878 | 4646 | 5414 | 6182 | 326 | 626 | 926 | C26 | F26 | 1226 | 1526 | 1826
Reserve |  | 807 | 1575 | 2343 | 3111 | 3879 | 4647 | 5415 | 6183 | 327 | 627 | 927 | C27 | F27 | 1227 | 1527 | 1827
Reserve |  | 808 | 1576 | 2344 | 3112 | 3880 | 4648 | 5416 | 6184 | 328 | 628 | 928 | C28 | F28 | 1228 | 1528 | 1828
Reserve |  | 809 | 1577 | 2345 | 3113 | 3881 | 4649 | 5417 | 6185 | 329 | 629 | 929 | C29 | F29 | 1229 | 1529 | 1829
Reserve |  | 810 | 1578 | 2346 | 3114 | 3882 | 4650 | 5418 | 6186 | 32A | 62A | 92A | C2A | F2A | 122A | 152A | 182A
Reserve |  | 811 | 1579 | 2347 | 3115 | 3883 | 4651 | 5419 | 6187 | 32B | 62B | 92B | C2B | F2B | 122B | 152B | 182B
Reserve |  | 812 | 1580 | 2348 | 3116 | 3884 | 4652 | 5420 | 6188 | 32C | 62C | 92C | C2C | F2C | 122C | 152C | 182C
Reserve |  | 813 | 1581 | 2349 | 3117 | 3885 | 4653 | 5421 | 6189 | 32D | 62D | 92D | C2D | F2D | 122D | 152D | 182D
Reserve |  | 814 | 1582 | 2350 | 3118 | 3886 | 4654 | 5422 | 6190 | 32E | 62E | 92E | C2E | F2E | 122E | 152E | 182E
Reserve |  | 815 | 1583 | 2351 | 3119 | 3887 | 4655 | 5423 | 6191 | 32F | 62F | 92F | C2F | F2F | 122F | 152F | 182F
Low-voltage switches | Compressor switching input 1 | 816 | 1584 | 2352 | 3120 | 3888 | 4656 | 5424 | 6192 | 330 | 630 | 930 | C30 | F30 | 1230 | 1530 | 1830 | System switch input | Reserve | 48 | 30
High-voltage switches |  | 817 | 1585 | 2353 | 3121 | 3889 | 4657 | 5425 | 6193 | 331 | 631 | 931 | C31 | F31 | 1231 | 1531 | 1831 |  | In-line switches | 49 | 31
Reserve |  | 818 | 1586 | 2354 | 3122 | 3890 | 4658 | 5426 | 6194 | 332 | 632 | 932 | C32 | F32 | 1232 | 1532 | 1832 |  | Reserve | 50 | 32
Reserve |  | 819 | 1587 | 2355 | 3123 | 3891 | 4659 | 5427 | 6195 | 333 | 633 | 933 | C33 | F33 | 1233 | 1533 | 1833 |  | Reserve | 51 | 33
Reserve |  | 820 | 1588 | 2356 | 3124 | 3892 | 4660 | 5428 | 6196 | 334 | 634 | 934 | C34 | F34 | 1234 | 1534 | 1834 |  | Reserve | 52 | 34
Reserve |  | 821 | 1589 | 2357 | 3125 | 3893 | 4661 | 5429 | 6197 | 335 | 635 | 935 | C35 | F35 | 1235 | 1535 | 1835 |  | Reserve | 53 | 35
Reserve |  | 822 | 1590 | 2358 | 3126 | 3894 | 4662 | 5430 | 6198 | 336 | 636 | 936 | C36 | F36 | 1236 | 1536 | 1836 |  | Reserve | 54 | 36
Reserve |  | 823 | 1591 | 2359 | 3127 | 3895 | 4663 | 5431 | 6199 | 337 | 637 | 937 | C37 | F37 | 1237 | 1537 | 1837 |  | Reserve | 55 | 37
Reserve |  | 824 | 1592 | 2360 | 3128 | 3896 | 4664 | 5432 | 6200 | 338 | 638 | 938 | C38 | F38 | 1238 | 1538 | 1838 |  | Tank electrical feedback | 56 | 38
Reserve |  | 825 | 1593 | 2361 | 3129 | 3897 | 4665 | 5433 | 6201 | 339 | 639 | 939 | C39 | F39 | 1239 | 1539 | 1839 |  | Thermostat C signal | 57 | 39
Reserve |  | 826 | 1594 | 2362 | 3130 | 3898 | 4666 | 5434 | 6202 | 33A | 63A | 93A | C3A | F3A | 123A | 153A | 183A |  | Thermostat H signal | 58 | 3A
Reserve |  | 827 | 1595 | 2363 | 3131 | 3899 | 4667 | 5435 | 6203 | 33B | 63B | 93B | C3B | F3B | 123B | 153B | 183B |  | Solar Signal | 59 | 3B
Reserve |  | 828 | 1596 | 2364 | 3132 | 3900 | 4668 | 5436 | 6204 | 33C | 63C | 93C | C3C | F3C | 123C | 153C | 183C |  | Smart Grid SG Signal | 60 | 3C
Reserve |  | 829 | 1597 | 2365 | 3133 | 3901 | 4669 | 5437 | 6205 | 33D | 63D | 93D | C3D | F3D | 123D | 153D | 183D |  | Smart grid EVU signal | 61 | 3D
Reserve |  | 830 | 1598 | 2366 | 3134 | 3902 | 4670 | 5438 | 6206 | 33E | 63E | 93E | C3E | F3E | 123E | 153E | 183E |  | Reserve | 62 | 3E
Reserve |  | 831 | 1599 | 2367 | 3135 | 3903 | 4671 | 5439 | 6207 | 33F | 63F | 93F | C3F | F3F | 123F | 153F | 183F |  | Reserve | 63 | 3F
Auxiliary electrical feedback | Unit switch input | 848 | 1616 | 2384 | 3152 | 3920 | 4688 | 5456 | 6224 | 350 | 650 | 950 | C50 | F50 | 1250 | 1550 | 1850
Water flow switch |  | 849 | 1617 | 2385 | 3153 | 3921 | 4689 | 5457 | 6225 | 351 | 651 | 951 | C51 | F51 | 1251 | 1551 | 1851
Reserve |  | 850 | 1618 | 2386 | 3154 | 3922 | 4690 | 5458 | 6226 | 352 | 652 | 952 | C52 | F52 | 1252 | 1552 | 1852
Reserve |  | 851 | 1619 | 2387 | 3155 | 3923 | 4691 | 5459 | 6227 | 353 | 653 | 953 | C53 | F53 | 1253 | 1553 | 1853
Reserve |  | 852 | 1620 | 2388 | 3156 | 3924 | 4692 | 5460 | 6228 | 354 | 654 | 954 | C54 | F54 | 1254 | 1554 | 1854
Reserve |  | 853 | 1621 | 2389 | 3157 | 3925 | 4693 | 5461 | 6229 | 355 | 655 | 955 | C55 | F55 | 1255 | 1555 | 1855
Reserve |  | 854 | 1622 | 2390 | 3158 | 3926 | 4694 | 5462 | 6230 | 356 | 656 | 956 | C56 | F56 | 1256 | 1556 | 1856
Reserve |  | 855 | 1623 | 2391 | 3159 | 3927 | 4695 | 5463 | 6231 | 357 | 657 | 957 | C57 | F57 | 1257 | 1557 | 1857
Reserve |  | 856 | 1624 | 2392 | 3160 | 3928 | 4696 | 5464 | 6232 | 358 | 658 | 958 | C58 | F58 | 1258 | 1558 | 1858
Reserve |  | 857 | 1625 | 2393 | 3161 | 3929 | 4697 | 5465 | 6233 | 359 | 659 | 959 | C59 | F59 | 1259 | 1559 | 1859
Reserve |  | 858 | 1626 | 2394 | 3162 | 3930 | 4698 | 5466 | 6234 | 35A | 65A | 95A | C5A | F5A | 125A | 155A | 185A
Reserve |  | 859 | 1627 | 2395 | 3163 | 3931 | 4699 | 5467 | 6235 | 35B | 65B | 95B | C5B | F5B | 125B | 155B | 185B
Reserve |  | 860 | 1628 | 2396 | 3164 | 3932 | 4700 | 5468 | 6236 | 35C | 65C | 95C | C5C | F5C | 125C | 155C | 185C
Reserve |  | 861 | 1629 | 2397 | 3165 | 3933 | 4701 | 5469 | 6237 | 35D | 65D | 95D | C5D | F5D | 125D | 155D | 185D
Reserve |  | 862 | 1630 | 2398 | 3166 | 3934 | 4702 | 5470 | 6238 | 35E | 65E | 95E | C5E | F5E | 125E | 155E | 185E
Reserve |  | 863 | 1631 | 2399 | 3167 | 3935 | 4703 | 5471 | 6239 | 35F | 65F | 95F | C5F | F5F | 125F | 155F | 185F

## 04-Fault
Read-only integer; Function code: 04
Point Name | Description | Address ( Decimal ) | [7 empty] | Address ( Hex ) | [7 empty] | Point Name | Description | Address ( Decimal ) | Address ( Hex )
|  | 0#Module | 1#Module | 2#Module | 3#Module | 4#Module | 5#Module | 6#Module | 7#Module | 0#Module | 1#Module | 2#Module | 3#Module | 4#Module | 5#Module | 6#Module | 7#Module
Compressor fault 1 | B0: Compressor low pressure B1: Compressor high pressure B2. B3. B4: Fin Temp. fault B5: Exhaust Temp. fault B6: Exhaust Temp. too high B7: J5 pressure sensor fault B8: J6 pressure sensor fault B9: Compressor low pressure too low B10: Compressor high pressure too high B11: Suction Temp. fault B12. B13: Suction air Temp. too low B14: Frequent emergency defrost B15: Abnormal Temp. difference between suction and exhaust | 1294 | 1550 | 1806 | 2062 | 2318 | 2574 | 2830 | 3086 | 50E | 60E | 70E | 80E | 90E | A0E | B0E | C0E | System fault 1 | B0. B1. B2: EEPROM data error B3. B4. B5: Total outlet water Temp. error B6: System maintenance data error B7. B8. B9. B10: Water tank electrical overload B11. B12: Hot water tank Temp. fault B13. B14: System total outlet water Temp. fault B15: Underfloor heating inlet water Temp. fault | 3342 | D0E
Compressor fault 2 | B0: Refrigeration evaporation too low B1. B2: Ambient Temp. restricts compressor from turning on B3: Plate change return water Temp. too low B4: Plate change return water Temp. too high B5: Fan 1 speed abnormal B6: Abnormal fan 2 speed B7. B8. B9. B10. B11: Inverter communication fault B12: Inverter fault B13: Inverter model setting in progress B14. B15: | 1295 | 1551 | 1807 | 2063 | 2319 | 2575 | 2831 | 3087 | 50F | 60F | 70F | 80F | 90F | A0F | B0F | C0F | System fault 2 | B0： Fan coil 01 communication fault B1： Fan coil 02 communication fault B2： Fan coil 03 communication fault B3： Fan coil 04 communication fault B4： Fan coil 05 communication fault B5： Fan coil 06 communication fault B6： Fan coil 07 communication fault B7： Fan coil 08 communication fault B8： Fan coil 09 communication fault B9： Fan coil 10 communication fault B10： Fan coil 11 communication fault B11： Fan coil 12 communication fault B12： Fan coil 13 communication fault B13： Fan coil 14 communication fault B14： Fan coil 15 communication fault B15： Fan coil 16 communication fault | 3343 | D0F
Compressor fault 3 | B0: Refrigerant gas side Temp. fault B1: Refrigerant liquid side Temp. fault B2: High evaporation Temp. | 1296 | 1552 | 1808 | 2064 | 2320 | 2576 | 2832 | 3088 | 510 | 610 | 710 | 810 | 910 | A10 | B10 | C10 | System fault 3 | B0： Fan coil 01 fault B1： Fan coil 02 fault B2： Fan coil 03 fault B3： Fan coil 04 fault B4： Fan coil 05 fault B5： Fan coil 06 fault B6： Fan coil 07 fault B7： Fan coil 08 fault B8： Fan coil 09 fault B9： Fan coil 10 fault B10： Fan coil 11 fault B11： Fan coil 12 fault B12： Fan coil 13 fault B13： Fan coil 14 fault B14： Fan coil 15 fault B15： Fan coil 16 fault | 3344 | D10
Unit fault 1 | B0: Ambient Temp. fault B1: Communication fault B2: EEPROM data error B3: Auxiliary electric heating overload B4: Water tank electrical heating overload B5: Plate exchange water outlet Temp. too low B6: Board exchange water outlet Temp. too high B7: Board exchange water outlet Temp. fault B8: Insufficient water flow B9. B10: Plate exchange return water Temp. fault B11: Total water discharge Temp. fault B12. B13: Plate exchange outlet and return Temp. difference is too large B14: Abnormal plate return Temp. difference B15: Inverter pump warning [80%] | 1298 | 1554 | 1810 | 2066 | 2322 | 2578 | 2834 | 3090 | 512 | 612 | 712 | 812 | 912 | A12 | B12 | C12 | System fault 4 | B0： Fan coil 17 communication fault B1： Fan coil 18 communication fault B2： Fan coil 19 communication fault B3： Fan coil 20 communication fault B4： Fan coil 21 communication fault B5： Fan coil 22 communication fault B6： Fan coil 23 communication fault B7： Fan coil 24 communication fault B8： Fan coil 25 communication fault B9： Fan coil 26 communication fault B10： Fan coil 27 communication fault B11： Fan coil 28 communication fault B12： Fan coil 29 communication fault B13： Fan coil 30 communication fault B14： Fan coil 31 communication fault B15： Fan coil 32 communication fault | 3345 | D11
Unit fault 2 | B0: Communication abnormality B1: Internal and external machine communication failure B2: Protocol version too low B3: Inverter pump fault B4: Abnormal model setting | 1299 | 1555 | 1811 | 2067 | 2323 | 2579 | 2835 | 3091 | 513 | 613 | 713 | 813 | 913 | A13 | B13 | C13 | System fault 5 | B0： Fan coil 17 fault B1： Fan coil 18 fault B2： Fan coil 19 fault B3： Fan coil 20 fault B4： Fan coil 21 fault B5： Fan coil 22 fault B6： Fan coil 23 fault B7： Fan coil 24 fault B8： Fan coil 25 fault B9： Fan coil 26 fault B10： Fan coil 27 fault B11： Fan coil 28 fault B12： Fan coil 29 fault B13： Fan coil 30 fault B14： Fan coil 31 fault B15： Fan coil 32 fault | 3346 | D12
[18 empty] | System fault 6 | B0: Buffer tank upper Temp. fault B1: Buffer tank lower Temp. fault B2: Solar Temp. fault B3: Wire controller communication fault B4: Air conditioner total water outlet Temp. fault B5: Indoor Temp. fault B6: Inverter water pump fault | 3347 | D13

## 02-Fault
Read-only integer; Function code: 04
Point Name | Description | Address ( Decimal ) | [7 empty] | Address ( Hex ) | [7 empty] | Point Name | Description | Address ( Decimal ) | Address ( Hex )
Low Pressure | Compressor Fault1 | 944 | 1712 | 2480 | 3248 | 4016 | 4784 | 5552 | 6320 | 3B0 | 6B0 | 9B0 | CB0 | FB0 | 12B0 | 15B0 | 18B0 | Reserve | System fault 1 | 176 | B0
High Pressure |  | 945 | 1713 | 2481 | 3249 | 4017 | 4785 | 5553 | 6321 | 3B1 | 6B1 | 9B1 | CB1 | FB1 | 12B1 | 15B1 | 18B1 | Reserve |  | 177 | B1
Reserve |  | 946 | 1714 | 2482 | 3250 | 4018 | 4786 | 5554 | 6322 | 3B2 | 6B2 | 9B2 | CB2 | FB2 | 12B2 | 15B2 | 18B2 | EEPROM data error |  | 178 | B2
Reserve |  | 947 | 1715 | 2483 | 3251 | 4019 | 4787 | 5555 | 6323 | 3B3 | 6B3 | 9B3 | CB3 | FB3 | 12B3 | 15B3 | 18B3 | Reserve |  | 179 | B3
Fin Temp. probe failure |  | 948 | 1716 | 2484 | 3252 | 4020 | 4788 | 5556 | 6324 | 3B4 | 6B4 | 9B4 | CB4 | FB4 | 12B4 | 15B4 | 18B4 | Reserve |  | 180 | B4
Exhaust air Temp. probe fault |  | 949 | 1717 | 2485 | 3253 | 4021 | 4789 | 5557 | 6325 | 3B5 | 6B5 | 9B5 | CB5 | FB5 | 12B5 | 15B5 | 18B5 | Total outlet Temp. error |  | 181 | B5
Exhaust air Temp. too high |  | 950 | 1718 | 2486 | 3254 | 4022 | 4790 | 5558 | 6326 | 3B6 | 6B6 | 9B6 | CB6 | FB6 | 12B6 | 15B6 | 18B6 | System maintenance data error |  | 182 | B6
J5 pressure sensor fault |  | 951 | 1719 | 2487 | 3255 | 4023 | 4791 | 5559 | 6327 | 3B7 | 6B7 | 9B7 | CB7 | FB7 | 12B7 | 15B7 | 18B7 | Reserve |  | 183 | B7
J6 pressure sensor fault |  | 952 | 1720 | 2488 | 3256 | 4024 | 4792 | 5560 | 6328 | 3B8 | 6B8 | 9B8 | CB8 | FB8 | 12B8 | 15B8 | 18B8 | Reserve |  | 184 | B8
Low pressure too low |  | 953 | 1721 | 2489 | 3257 | 4025 | 4793 | 5561 | 6329 | 3B9 | 6B9 | 9B9 | CB9 | FB9 | 12B9 | 15B9 | 18B9 | Reserve |  | 185 | B9
High pressure too high |  | 954 | 1722 | 2490 | 3258 | 4026 | 4794 | 5562 | 6330 | 3BA | 6BA | 9BA | CBA | FBA | 12BA | 15BA | 18BA | Water tank electrical overload |  | 186 | BA
Suction Temp. fault |  | 955 | 1723 | 2491 | 3259 | 4027 | 4795 | 5563 | 6331 | 3BB | 6BB | 9BB | CBB | FBB | 12BB | 15BB | 18BB | Reserve |  | 187 | BB
Reserve |  | 956 | 1724 | 2492 | 3260 | 4028 | 4796 | 5564 | 6332 | 3BC | 6BC | 9BC | CBC | FBC | 12BC | 15BC | 18BC | Hot water tank Temp. fault |  | 188 | BC
Low suction Temp. |  | 957 | 1725 | 2493 | 3261 | 4029 | 4797 | 5565 | 6333 | 3BD | 6BD | 9BD | CBD | FBD | 12BD | 15BD | 18BD | Reserve |  | 189 | BD
Frequent emergency defrosts |  | 958 | 1726 | 2494 | 3262 | 4030 | 4798 | 5566 | 6334 | 3BE | 6BE | 9BE | CBE | FBE | 12BE | 15BE | 18BE | Total system outlet Temp. fault |  | 190 | BE
Abnormal Temp. difference between suction and exhaust |  | 959 | 1727 | 2495 | 3263 | 4031 | 4799 | 5567 | 6335 | 3BF | 6BF | 9BF | CBF | FBF | 12BF | 15BF | 18BF | Underfloor heating inlet Temp. fault |  | 191 | BF
Cooling evaporation too low | Compressor Fault2 | 960 | 1728 | 2496 | 3264 | 4032 | 4800 | 5568 | 6336 | 3C0 | 6C0 | 9C0 | CC0 | FC0 | 12C0 | 15C0 | 18C0 | Reserve | System fault 2 | 192 | C0
Reserve |  | 961 | 1729 | 2497 | 3265 | 4033 | 4801 | 5569 | 6337 | 3C1 | 6C1 | 9C1 | CC1 | FC1 | 12C1 | 15C1 | 18C1 | Reserve |  | 193 | C1
Ambient Temp. restricts compressor turn-on |  | 962 | 1730 | 2498 | 3266 | 4034 | 4802 | 5570 | 6338 | 3C2 | 6C2 | 9C2 | CC2 | FC2 | 12C2 | 15C2 | 18C2 | Reserve |  | 194 | C2
Low plate exchange return water Temp. |  | 963 | 1731 | 2499 | 3267 | 4035 | 4803 | 5571 | 6339 | 3C3 | 6C3 | 9C3 | CC3 | FC3 | 12C3 | 15C3 | 18C3 | Reserve |  | 195 | C3
Plate exchange return water Temp. too high |  | 964 | 1732 | 2500 | 3268 | 4036 | 4804 | 5572 | 6340 | 3C4 | 6C4 | 9C4 | CC4 | FC4 | 12C4 | 15C4 | 18C4 | Reserve |  | 196 | C4
Abnormal speed of fan 1 |  | 965 | 1733 | 2501 | 3269 | 4037 | 4805 | 5573 | 6341 | 3C5 | 6C5 | 9C5 | CC5 | FC5 | 12C5 | 15C5 | 18C5 | Reserve |  | 197 | C5
Abnormal speed of fan 2 |  | 966 | 1734 | 2502 | 3270 | 4038 | 4806 | 5574 | 6342 | 3C6 | 6C6 | 9C6 | CC6 | FC6 | 12C6 | 15C6 | 18C6 | Reserve |  | 198 | C6
Reserve |  | 967 | 1735 | 2503 | 3271 | 4039 | 4807 | 5575 | 6343 | 3C7 | 6C7 | 9C7 | CC7 | FC7 | 12C7 | 15C7 | 18C7 | Reserve |  | 199 | C7
Reserve |  | 968 | 1736 | 2504 | 3272 | 4040 | 4808 | 5576 | 6344 | 3C8 | 6C8 | 9C8 | CC8 | FC8 | 12C8 | 15C8 | 18C8 | Reserve |  | 200 | C8
Reserve |  | 969 | 1737 | 2505 | 3273 | 4041 | 4809 | 5577 | 6345 | 3C9 | 6C9 | 9C9 | CC9 | FC9 | 12C9 | 15C9 | 18C9 | Reserve |  | 201 | C9
Reserve |  | 970 | 1738 | 2506 | 3274 | 4042 | 4810 | 5578 | 6346 | 3CA | 6CA | 9CA | CCA | FCA | 12CA | 15CA | 18CA | Reserve |  | 202 | CA
Inverter communication faults |  | 971 | 1739 | 2507 | 3275 | 4043 | 4811 | 5579 | 6347 | 3CB | 6CB | 9CB | CCB | FCB | 12CB | 15CB | 18CB | Reserve |  | 203 | CB
Inverter fault |  | 972 | 1740 | 2508 | 3276 | 4044 | 4812 | 5580 | 6348 | 3CC | 6CC | 9CC | CCC | FCC | 12CC | 15CC | 18CC | Reserve |  | 204 | CC
Inverter model setting in progress |  | 973 | 1741 | 2509 | 3277 | 4045 | 4813 | 5581 | 6349 | 3CD | 6CD | 9CD | CCD | FCD | 12CD | 15CD | 18CD | Reserve |  | 205 | CD
Reserve |  | 974 | 1742 | 2510 | 3278 | 4046 | 4814 | 5582 | 6350 | 3CE | 6CE | 9CE | CCE | FCE | 12CE | 15CE | 18CE | Reserve |  | 206 | CE
Reserve |  | 975 | 1743 | 2511 | 3279 | 4047 | 4815 | 5583 | 6351 | 3CF | 6CF | 9CF | CCF | FCF | 12CF | 15CF | 18CF | Reserve |  | 207 | CF
Refrigerant gas side Temp. fault | Compressor Fault3 | 976 | 1744 | 2512 | 3280 | 4048 | 4816 | 5584 | 6352 | 3D0 | 6D0 | 9D0 | CD0 | FD0 | 12D0 | 15D0 | 18D0 | Reserve | System fault 3 | 208 | D0
Refrigerant liquid side Temp. fault |  | 977 | 1745 | 2513 | 3281 | 4049 | 4817 | 5585 | 6353 | 3D1 | 6D1 | 9D1 | CD1 | FD1 | 12D1 | 15D1 | 18D1 | Reserve |  | 209 | D1
Evaporation Temp. too high |  | 978 | 1746 | 2514 | 3282 | 4050 | 4818 | 5586 | 6354 | 3D2 | 6D2 | 9D2 | CD2 | FD2 | 12D2 | 15D2 | 18D2 | Reserve |  | 210 | D2
Reserve |  | 979 | 1747 | 2515 | 3283 | 4051 | 4819 | 5587 | 6355 | 3D3 | 6D3 | 9D3 | CD3 | FD3 | 12D3 | 15D3 | 18D3 | Reserve |  | 211 | D3
Reserve |  | 980 | 1748 | 2516 | 3284 | 4052 | 4820 | 5588 | 6356 | 3D4 | 6D4 | 9D4 | CD4 | FD4 | 12D4 | 15D4 | 18D4 | Reserve |  | 212 | D4
Reserve |  | 981 | 1749 | 2517 | 3285 | 4053 | 4821 | 5589 | 6357 | 3D5 | 6D5 | 9D5 | CD5 | FD5 | 12D5 | 15D5 | 18D5 | Reserve |  | 213 | D5
Reserve |  | 982 | 1750 | 2518 | 3286 | 4054 | 4822 | 5590 | 6358 | 3D6 | 6D6 | 9D6 | CD6 | FD6 | 12D6 | 15D6 | 18D6 | Reserve |  | 214 | D6
Reserve |  | 983 | 1751 | 2519 | 3287 | 4055 | 4823 | 5591 | 6359 | 3D7 | 6D7 | 9D7 | CD7 | FD7 | 12D7 | 15D7 | 18D7 | Reserve |  | 215 | D7
Reserve |  | 984 | 1752 | 2520 | 3288 | 4056 | 4824 | 5592 | 6360 | 3D8 | 6D8 | 9D8 | CD8 | FD8 | 12D8 | 15D8 | 18D8 | Reserve |  | 216 | D8
Reserve |  | 985 | 1753 | 2521 | 3289 | 4057 | 4825 | 5593 | 6361 | 3D9 | 6D9 | 9D9 | CD9 | FD9 | 12D9 | 15D9 | 18D9 | Reserve |  | 217 | D9
Reserve |  | 986 | 1754 | 2522 | 3290 | 4058 | 4826 | 5594 | 6362 | 3DA | 6DA | 9DA | CDA | FDA | 12DA | 15DA | 18DA | Reserve |  | 218 | DA
Reserve |  | 987 | 1755 | 2523 | 3291 | 4059 | 4827 | 5595 | 6363 | 3DB | 6DB | 9DB | CDB | FDB | 12DB | 15DB | 18DB | Reserve |  | 219 | DB
Reserve |  | 988 | 1756 | 2524 | 3292 | 4060 | 4828 | 5596 | 6364 | 3DC | 6DC | 9DC | CDC | FDC | 12DC | 15DC | 18DC | Reserve |  | 220 | DC
Reserve |  | 989 | 1757 | 2525 | 3293 | 4061 | 4829 | 5597 | 6365 | 3DD | 6DD | 9DD | CDD | FDD | 12DD | 15DD | 18DD | Reserve |  | 221 | DD
Reserve |  | 990 | 1758 | 2526 | 3294 | 4062 | 4830 | 5598 | 6366 | 3DE | 6DE | 9DE | CDE | FDE | 12DE | 15DE | 18DE | Reserve |  | 222 | DE
Reserve |  | 991 | 1759 | 2527 | 3295 | 4063 | 4831 | 5599 | 6367 | 3DF | 6DF | 9DF | CDF | FDF | 12DF | 15DF | 18DF | Reserve |  | 223 | DF
Module ambient Temp. failure | Unit Fault1 | 1008 | 1776 | 2544 | 3312 | 4080 | 4848 | 5616 | 6384 | 3F0 | 6F0 | 9F0 | CF0 | FF0 | 12F0 | 15F0 | 18F0 | Reserve | System fault 4 | 224 | E0
Communication fault |  | 1009 | 1777 | 2545 | 3313 | 4081 | 4849 | 5617 | 6385 | 3F1 | 6F1 | 9F1 | CF1 | FF1 | 12F1 | 15F1 | 18F1 | Reserve |  | 225 | E1
EEPROM data error |  | 1010 | 1778 | 2546 | 3314 | 4082 | 4850 | 5618 | 6386 | 3F2 | 6F2 | 9F2 | CF2 | FF2 | 12F2 | 15F2 | 18F2 | Reserve |  | 226 | E2
Auxiliary electrical overload |  | 1011 | 1779 | 2547 | 3315 | 4083 | 4851 | 5619 | 6387 | 3F3 | 6F3 | 9F3 | CF3 | FF3 | 12F3 | 15F3 | 18F3 | Reserve |  | 227 | E3
Water tank electrical overload |  | 1012 | 1780 | 2548 | 3316 | 4084 | 4852 | 5620 | 6388 | 3F4 | 6F4 | 9F4 | CF4 | FF4 | 12F4 | 15F4 | 18F4 | Reserve |  | 228 | E4
Plate exchanger outlet water Temp. too low |  | 1013 | 1781 | 2549 | 3317 | 4085 | 4853 | 5621 | 6389 | 3F5 | 6F5 | 9F5 | CF5 | FF5 | 12F5 | 15F5 | 18F5 | Reserve |  | 229 | E5
Plate exchanger outlet water Temp. too high |  | 1014 | 1782 | 2550 | 3318 | 4086 | 4854 | 5622 | 6390 | 3F6 | 6F6 | 9F6 | CF6 | FF6 | 12F6 | 15F6 | 18F6 | Reserve |  | 230 | E6
Plate change water Temp. fault |  | 1015 | 1783 | 2551 | 3319 | 4087 | 4855 | 5623 | 6391 | 3F7 | 6F7 | 9F7 | CF7 | FF7 | 12F7 | 15F7 | 18F7 | Reserve |  | 231 | E7
Insufficient water flow |  | 1016 | 1784 | 2552 | 3320 | 4088 | 4856 | 5624 | 6392 | 3F8 | 6F8 | 9F8 | CF8 | FF8 | 12F8 | 15F8 | 18F8 | Reserve |  | 232 | E8
Reserve |  | 1017 | 1785 | 2553 | 3321 | 4089 | 4857 | 5625 | 6393 | 3F9 | 6F9 | 9F9 | CF9 | FF9 | 12F9 | 15F9 | 18F9 | Reserve |  | 233 | E9
Out and return water Temp. difference is too large |  | 1018 | 1786 | 2554 | 3322 | 4090 | 4858 | 5626 | 6394 | 3FA | 6FA | 9FA | CFA | FFA | 12FA | 15FA | 18FA | Reserve |  | 234 | EA
Total discharge Temp. fault |  | 1019 | 1787 | 2555 | 3323 | 4091 | 4859 | 5627 | 6395 | 3FB | 6FB | 9FB | CFB | FFB | 12FB | 15FB | 18FB | Reserve |  | 235 | EB
Reserve |  | 1020 | 1788 | 2556 | 3324 | 4092 | 4860 | 5628 | 6396 | 3FC | 6FC | 9FC | CFC | FFC | 12FC | 15FC | 18FC | Reserve |  | 236 | EC
Excessive difference in plate return Temp. |  | 1021 | 1789 | 2557 | 3325 | 4093 | 4861 | 5629 | 6397 | 3FD | 6FD | 9FD | CFD | FFD | 12FD | 15FD | 18FD | Reserve |  | 237 | ED
Out and return water Temp. difference abnormal |  | 1022 | 1790 | 2558 | 3326 | 4094 | 4862 | 5630 | 6398 | 3FE | 6FE | 9FE | CFE | FFE | 12FE | 15FE | 18FE | Reserve |  | 238 | EE
Inverter pump warning [80%] |  | 1023 | 1791 | 2559 | 3327 | 4095 | 4863 | 5631 | 6399 | 3FF | 6FF | 9FF | CFF | FFF | 12FF | 15FF | 18FF | Reserve |  | 239 | EF
Communication abnormal | Unit Fault2 | 1024 | 1792 | 2560 | 3328 | 4096 | 4864 | 5632 | 6400 | 400 | 700 | A00 | D00 | 1000 | 1300 | 1600 | 1900 | Reserve | System fault 5 | 240 | F0
Internal and external machine communication fault |  | 1025 | 1793 | 2561 | 3329 | 4097 | 4865 | 5633 | 6401 | 401 | 701 | A01 | D01 | 1001 | 1301 | 1601 | 1901 | Reserve |  | 241 | F1
Protocol version too low |  | 1026 | 1794 | 2562 | 3330 | 4098 | 4866 | 5634 | 6402 | 402 | 702 | A02 | D02 | 1002 | 1302 | 1602 | 1902 | Reserve |  | 242 | F2
Inverter pump fault |  | 1027 | 1795 | 2563 | 3331 | 4099 | 4867 | 5635 | 6403 | 403 | 703 | A03 | D03 | 1003 | 1303 | 1603 | 1903 | Reserve |  | 243 | F3
Abnormal model setting |  | 1028 | 1796 | 2564 | 3332 | 4100 | 4868 | 5636 | 6404 | 404 | 704 | A04 | D04 | 1004 | 1304 | 1604 | 1904 | Reserve |  | 244 | F4
Reserve |  | 1029 | 1797 | 2565 | 3333 | 4101 | 4869 | 5637 | 6405 | 405 | 705 | A05 | D05 | 1005 | 1305 | 1605 | 1905 | Reserve |  | 245 | F5
Reserve |  | 1030 | 1798 | 2566 | 3334 | 4102 | 4870 | 5638 | 6406 | 406 | 706 | A06 | D06 | 1006 | 1306 | 1606 | 1906 | Reserve |  | 246 | F6
Reserve |  | 1031 | 1799 | 2567 | 3335 | 4103 | 4871 | 5639 | 6407 | 407 | 707 | A07 | D07 | 1007 | 1307 | 1607 | 1907 | Reserve |  | 247 | F7
Reserve |  | 1032 | 1800 | 2568 | 3336 | 4104 | 4872 | 5640 | 6408 | 408 | 708 | A08 | D08 | 1008 | 1308 | 1608 | 1908 | Reserve |  | 248 | F8
Reserve |  | 1033 | 1801 | 2569 | 3337 | 4105 | 4873 | 5641 | 6409 | 409 | 709 | A09 | D09 | 1009 | 1309 | 1609 | 1909 | Reserve |  | 249 | F9
Reserve |  | 1034 | 1802 | 2570 | 3338 | 4106 | 4874 | 5642 | 6410 | 40A | 70A | A0A | D0A | 100A | 130A | 160A | 190A | Reserve |  | 250 | FA
Reserve |  | 1035 | 1803 | 2571 | 3339 | 4107 | 4875 | 5643 | 6411 | 40B | 70B | A0B | D0B | 100B | 130B | 160B | 190B | Reserve |  | 251 | FB
Reserve |  | 1036 | 1804 | 2572 | 3340 | 4108 | 4876 | 5644 | 6412 | 40C | 70C | A0C | D0C | 100C | 130C | 160C | 190C | Reserve |  | 252 | FC
Reserve |  | 1037 | 1805 | 2573 | 3341 | 4109 | 4877 | 5645 | 6413 | 40D | 70D | A0D | D0D | 100D | 130D | 160D | 190D | Reserve |  | 253 | FD
Reserve |  | 1038 | 1806 | 2574 | 3342 | 4110 | 4878 | 5646 | 6414 | 40E | 70E | A0E | D0E | 100E | 130E | 160E | 190E | Reserve |  | 254 | FE
Reserve |  | 1039 | 1807 | 2575 | 3343 | 4111 | 4879 | 5647 | 6415 | 40F | 70F | A0F | D0F | 100F | 130F | 160F | 190F | Reserve |  | 255 | FF
[18 empty] | Buffer tank upper Temp. fault | System fault 6 | 256 | 100
[18 empty] | Buffer tank lower Temp. fault |  | 257 | 101
[18 empty] | Solar Temp. fault |  | 258 | 102
[18 empty] | Wire controller communication fault |  | 259 | 103
[18 empty] | Air conditioning total outlet Temp. fault |  | 260 | 104
[18 empty] | Indoor Temp. fault |  | 261 | 105
[18 empty] | Inverter pump fault |  | 262 | 106
[18 empty] | Reserve |  | 263 | 107
[18 empty] | Reserve |  | 264 | 108
[18 empty] | Reserve |  | 265 | 109
[18 empty] | Reserve |  | 266 | 10A
[18 empty] | Reserve |  | 267 | 10B
[18 empty] | Reserve |  | 268 | 10C
[18 empty] | Reserve |  | 269 | 10D
[18 empty] | Reserve |  | 270 | 10E
[18 empty] | Reserve |  | 271 | 10F

## Parameters
Parameters | No. | Description | Range | Unit | Permissions | Default value | address
User parameter | 1 | Control modes | [1] Cooling; [2] Heating; [3] Automatic | / | The Factory | Heating | 6400
User parameter | 2 | Cooling set temperature | -15...35 | ℃ | The Factory | 5 | 6401
User parameter | 3 | Heating set temperature | 0...85 | ℃ | The Factory | 60 | 6402
User parameter | 4 | Hot water set temperature | 0...80 | ℃ | The Factory | 55 | 6403
User parameter | 5 | Cooling set room temperature | 16...30 | ℃ | The Factory | 26 | 6404
User parameter | 6 | Heating set room temperature | 16...30 | ℃ | The Factory | 20 | 6405
User parameter | 9 | Heating set temperature (B) | 40...60 | ℃ | The Factory | 60 | 6408
User parameter | 10 | Heating set room temperature (B) | 16...30 | ℃ | The Factory | 26 | 6409
User parameter | 11 | Power mode | [0] Standard; [1] Powerful; [2] Eco; [3] Automatic | / | User | Standard | 6410
User parameter | 13 | Timed sterilisation function | [0] Disable; [1] Use | / | User | Disable | 6412
User parameter | 14 | Sterilisation temperature | 60...70 | ℃ | User | 65 | 6413
User parameter | 15 | Sterilisation maximum cycle | 90...300 | 分 | User | 210 | 6414
User parameter | 16 | Sterilisation high temperature time | 5...60 | 分 | User | 15 | 6415
User parameter | 26 | A-zone cooling curve | [0] disabled; [1] low temperature curve 1; [2] low temperature curve 2; [3] low temperature curve 3; [4] low temperature curve 4; [5] low temperature curve 5; [6] low temperature curve 6; [7] low temperature curve 7; [8] low temperature curve 8; [9] high temperature curve 1; [10] high temperature curve 2; [11] high temperature curve 3; [12] high temperature curve 4; [13] high temperature curve 5; [14 ] high temperature curve 6;[15] high temperature curve 7;[16] high temperature curve 8;[17] curve 9 | / | User | Disable | 6425
User parameter | 27 | A zone heating curve | [0] disabled; [1] low temperature curve 1; [2] low temperature curve 2; [3] low temperature curve 3; [4] low temperature curve 4; [5] low temperature curve 5; [6] low temperature curve 6; [7] low temperature curve 7; [8] low temperature curve 8; [9] high temperature curve 1; [10] high temperature curve 2; [11] high temperature curve 3; [12] high temperature curve 4; [13] high temperature curve 5; [14 ] high temperature curve 6;[15] high temperature curve 7;[16] high temperature curve 8;[17] curve 9 | / | User | Disable | 6426
User parameter | 28 | Zone B cooling curve | [0] disabled; [1] low temperature curve 1; [2] low temperature curve 2; [3] low temperature curve 3; [4] low temperature curve 4; [5] low temperature curve 5; [6] low temperature curve 6; [7] low temperature curve 7; [8] low temperature curve 8; [9] high temperature curve 1; [10] high temperature curve 2; [11] high temperature curve 3; [12] high temperature curve 4; [13] high temperature curve 5; [14 ] high temperature curve 6;[15] high temperature curve 7;[16] high temperature curve 8;[17] curve 9 | / | User | Disable | 6427
User parameter | 29 | Zone B heating curve | [0] disabled; [1] low temperature curve 1; [2] low temperature curve 2; [3] low temperature curve 3; [4] low temperature curve 4; [5] low temperature curve 5; [6] low temperature curve 6; [7] low temperature curve 7; [8] low temperature curve 8; [9] high temperature curve 1; [10] high temperature curve 2; [11] high temperature curve 3; [12] high temperature curve 4; [13] high temperature curve 5; [14 ] high temperature curve 6;[15] high temperature curve 7;[16] high temperature curve 8;[17] curve 9 | / | User | Disable | 6428
User parameter | 30 | Curve 9 Cooling ambient temperature1 | -5...46 | ℃ | User | 35 | 6429
User parameter | 31 | Curve 9 Cooling ambient temperature 2 | -5...46 | ℃ | User | 25 | 6430
User parameter | 32 | Curve 9 Cooling outlet temperature 1 | 5...25 | ℃ | User | 10 | 6431
User parameter | 33 | Curve 9 Cooling outlet temperature 2 | 5...25 | ℃ | User | 16 | 6432
User parameter | 34 | Curve 9 Heating ambient temperature 1 | -25...35 | ℃ | User | 7 | 6433
User parameter | 35 | Curve 9 Heating ambient temperature2 | -25...35 | ℃ | User | -5 | 6434
User parameter | 36 | Curve 9 Heating outlet temperature1 | 25...65 | ℃ | User | 28 | 6435
User parameter | 37 | Curve 9 Heating outlet temperature2 | 25...65 | ℃ | User | 35 | 6436
User parameter | 29 | Auxiliary Electric Heater | 0-Disable、1-Enable | / | 0 | Disable | 7189
User parameter | 30 | Auxiliary Heater Gear Set | 1~3 | / | 0 | 1 | 7193
User parameter | 31 | DHW Electric Heater | 0-Disable、1-Enable | / | 0 | Disable | 6491
User parameter | 32 | DHW temperature startup difference | -20.0~20.0 | ℃ | 1 | 4 | 6481
User parameter | 42 | Temperature Turn on difference of cooling | -20.0~20.0 | ℃ | 1 | 2 | 7169
User parameter | 43 | Temperature Turn off difference of cooling | -20.0~20.0 | ℃ | 1 | 4 | 7170
User parameter | 44 | Temperature Turn on difference of heating | -20.0~20.0 | ℃ | 1 | 2 | 7171
User parameter | 45 | Temperature Turn off difference of heating | -20.0~20.0 | ℃ | 1 | 2 | 7172